***********************************************

*                                             *

*          Fluid Flow Calculations            *

*                                             *

*               Version 1.2                   *

*                                             *

*                                             *

*     Copyright 1992 by Frank M. DeBlanc      *

*                                             *

***********************************************

This program is used to solve fluid flow

problems using the Darcy-Weisbach equation.

The author of this program is:

Frank M. DeBlanc

2202 Mary Margaret Drive

St. Martinville, Louisiana  70582

Table of Contents

Page

I.     Shareware Registration Form ...........................  1

II.    Disclaimer ............................................  2

III.   User Supported Software Concept .......................  2

IV.    Files Used With Fluid Flow Calculations................  3

V.     Introduction ..........................................  3

VI.    First Time Use ........................................  4

VII.   Enhancements and Improvements .........................  4

VIII.  Special Input..........................................  4

A.  How to Input Scientific Notation..............  4

B.  If you want to use kinematic viscosity........  4

IX.    Menu Usage ............................................  5

X.     Using Fluid Flow Calculations .........................  5

A.  Fluid Flow Calculations.......................  6

1.  Head Loss................................  6

2.  Fluid Flow...............................  6

3.  Diameter.................................  7

4.  2 Parallel Pipes.........................  7

5.  2 Series Pipes...........................  7

6.  Head Loss - Non-Circular Conduit.........  8

7.  Fluid Flow - Non-Circular Conduit........  8

8.  Diameter - Non-Circular Conduit..........  8

B.  Hydraulic Radius..............................  8

C.  Properties....................................  9

1.  Water....................................  9

2.  Air......................................  9

D.  Options....................................... 10

XI.  Examples................................................. 10

A.  Circular Conduit.............................. 10

1.  Solve for head loss...................... 10

2.  Solve for fluid flow..................... 11

3.  Solve for diameter....................... 11

B.  Non-Circular Conduit.......................... 12

1.  Solve for head loss...................... 12

2.  Solve for fluid flow..................... 13

3.  Solve for fluid flow (open channel flow). 14

C.  Two parallel pipes............................ 15

D.  Two series pipes.............................. 16

Fluid Flow Calculations 1.2

User Supported Software

-------------------------------

I.  Registration and Order Form

-------------------------------

Registration of currently used Fluid Flow Calculations   $23.00

plus $5.00 Shipping & Handling

Version Number 1.2

Number of Copies......................................______

Subtotal..............................................______

Shipping & Handling...................................$5.00

Total.................................................______

Disk size required   720 k - 3.5" _____    360 k - 5.25" _____

Your Address:

__________________________________

Name

__________________________________

Address

__________________________________

City

__________________________________

State                  Zip

---------------------------------------------------------------------------

I obtained my copy of Fluid Flow Calculations from:

____________________________________________________________________________

Comments:

----------------------------------------------------------------------------

Send Order To:

Frank M. DeBlanc

2202 Mary Margaret Drive

St. Martinville, Louisiana  70582

-----------------------------------------------------------------------------

============================================================================

Fluid Flow Cal Version 1.2  Copyright 1992 by Frank DeBlanc   Page 2

============================================================================

-------------------------------------------------------------------

II.  Disclaimer

-------------------------------------------------------------------

FRANK M. DEBLANC DISCLAIMS ALL WARRANTIES RELATING TO THIS SOFTWARE,

WHETHER EXPRESS OR IMPLIED, INCLUDING BUT NOT LIMITED TO ANY IMPLIED

WARRANTIES OF MERCHANTABILITY AND FITNESS FOR A PARTICULAR PURPOSE,

AND ALL SUCH WARRANTIES ARE EXPRESSLY AND SPECIFICALLY DISCLAIMED.

NEITHER FRANK M. DEBLANC NOR ANYONE ELSE WHO HAS BEEN INVOLVED IN THE

CREATION, PRODUCTION, OR DELIVERY OF THIS SOFTWARE SHALL BE LIABLE

FOR ANY INDIRECT, CONSEQUENTIAL, OR INCIDENTAL DAMAGES ARISING OUT OF

THE USE OR INABILITY TO USE SUCH SOFTWARE EVEN IF FRANK M. DEBLANC

HAD BEEN ADVISED OF THE POSSIBILITY OF SUCH DAMAGES OR CLAIMS.  IN NO

EVENT SHALL FRANK M. DEBLANC'S LIABILITY FOR ANY DAMAGES EVER EXCEED

THE PRICE PAID FOR THE LICENSE TO USE THE SOFTWARE, REGARDLESS OF THE

FORM OF CLAIM.  THE PERSON USING THE SOFTWARE BEARS ALL RISK AS TO THE

QUALITY AND PERFORMANCE OF THE SOFTWARE.

Some states do not allow the exclusion of the limit of liability

for consequential or incidental damages, so the above limitation may

not be apply to you.

This agreement shall be governed by the laws of the State of

Louisiana and shall inure to the benefit of Frank M. DeBlanc and any

successors, administrators, heirs and assigns.  Any action proceeding

brought by either party against the other arising out of or related

to this agreement shall be brought only in a STATE or FEDERAL COURT

of competent jurisdiction closest to St. Martin Parish, Louisiana.

The parties hereby consent to in personam jurisdiction of said courts.

********************************************************************

--------------------------------------------------------------------

III.  User Supported Software Concept

--------------------------------------------------------------------

This version of Fluid Flow Calculations is a "shareware program"

and is provided at no charge to the user for evaluation.  Shareware

is a distribution method, not a type of software.  You get to try

this program before you buy.  Fluid Flow Calculations has the ultimate

guarantee--if you don't use the product, you don't pay for it.  On the

other hand, if you do use this product and find it of value then the

cost is $23.  Feel free to share it with your friends, but please do

not give it away altered. Upon receipt of your payment, you will become

a registered owner of Fluid Flow Cal.  I will then send you a copy of

the program that will not have the shareware nag screen.  You will

receive free technical support for 90 days (by mail).

Registered users can also update to later versions for a

nominal update fee of $7.00

Please address all registration requests and customer support

inquires to:

Frank M. DeBlanc

2202 Mary Margaret Drive

St. Martinville, Louisiana  70582

**********************************************************************

============================================================================

Fluid Flow Cal Version 1.2  Copyright 1992 by Frank DeBlanc   Page 3

============================================================================

----------------------------------------------------------------------

IV.  Files used with Fluid Flow Calculations

----------------------------------------------------------------------

FLUIDS.EXE     (Used to start the program)

README.DOC     (This file)

VENDOR.DOC     (File for disk distributors & user groups)

PRINTDOC.BAT   (File to print out this document)

COLOR          (File for optional background and foreground

colors)

*******************************************************************

-------------------------------------------------------------------

V.  Introduction

-------------------------------------------------------------------

Purpose of the Program:

This program is used to solve fluid flow problems.

1.  Find head loss (circular & non-circular conduits)

or

2.  Find fluid flow (circular & non-circular conduits)

or

3.  Find pipe diameter  (circular & non-circular conduits)

or

4.  Two parallel pipes  (circular conduits)

or

5.  Two series pipes (circular conduits)

or

6.  Hydraulic radius

Fluid Flow Calculations uses the Darcey-Weisbach equation,

one of the most widely used equations for pipe flow.  It is valid

for laminar or turbulent flow in all fluids.  When using the Darcey-Weisbach

equation one must use the Moody diagram to look up the friction factor.

Also, when using the equation one must resort to trial-and-error

calculations when solving for fluid flow and pipe diameter.  With

this program there is no need for trial-and-error calculations or

having to use the Moody diagram.  This will not only save you time

but will also reduce the possibility of a calculation error or a

looking-it-up-in-the-table error.

Types of problems solved by this program:

1.  Full flowing circular pipes.

2.  Partially full circular pipes.

3.  Non-circular full flowing pipes

4.  Non-circular partially full flowing pipes.

5.  Open channel flow.

****************************************************************************

============================================================================

Fluid Flow Cal Version 1.2  Copyright 1992 by Frank DeBlanc   Page 4

============================================================================

-------------------------------------------------------------------

VI.  First Time Use

-------------------------------------------------------------------

Before using Fluid Flow Cal for the first time, it is a good

idea to make a backup copy.  When using on a hard drive please

place the files in a subdirectory.  Do not place files in the

root directory (C:\).

Example:

C:\ffc12    [possible directory to place files]

To copy files to this directory:

copy *.* c:\ffc12

********************************************************************

---------------------------------------------------------------------------

VII.  Enhancements and Improvements

---------------------------------------------------------------------------

Version 1.2 has the following not found in version 1.1.

1.  New menu for easier operation.

2.  Two series pipes.

3.  Table for water and air properties.

4.  Fluid Flow default bug has been fixed.

5.  Non-circular Conduits & Open Channel Flow.

****************************************************************************

---------------------------------------------------------------------------

VIII.  Special Input

---------------------------------------------------------------------------

A.  How to Input Scientific Notation

.0000273 is input as  2.73d-5

273000 is input as 2.73d5

.00344 is input as 3.44d-3

450 is input as 4.5d2

B.  If you want to use kinematic viscosity.

Suppose you want to use kinematic viscosity instead of absolute

viscosity.  All you have to do is input the specific weight as

32.2 lbf/cubic foot and when asked to input the absolute viscosity

just input the kinematic viscosity instead (square ft/sec).

Note:  mass flow rate, specific weight, pressure drop per 100 ft,

and absolute viscosity will be reported incorrectly.  Just ignore

those values.  All other values will be correct.

****************************************************************************

============================================================================

Fluid Flow Cal Version 1.2  Copyright 1992 by Frank DeBlanc   Page 5

============================================================================

---------------------------------------------------------------------------

IX.  Menu Usage

---------------------------------------------------------------------------

If you have a mouse you may choose your selection by pressing

the left mouse button while pointing at the desired location.  When

using the main menu without a mouse then you must hold down the

<alt> key and press the first letter of the menu item you want to

choose.  An example of this is:  Suppose you want to choose "options"

from the main menu.  All you have to do is hold down the <alt> key

and press the "o".

<alt> f   --->  Fluid Flow Calculations

<alt> h   --->  Hydraulic Radius

<alt> p   --->  Properties

<alt> o   --->  Options

<alt> e   --->  Exit

Use the arrow keys to move through the menu.  When

using the arrow keys to point to a selection you must hit the

<return> or <enter> key to execute.

When inputting data and you want to discontinue with the data

then just press the escape key or with your mouse press the left

mouse button over the little solid square in the upper left hand

corner of the input box.

****************************************************************************

---------------------------------------------------------------------------

X.  Using Fluid Flow Calculations

---------------------------------------------------------------------------

To start the program type in "Fluids".  The first screen that appears

is the shareware "nag" screen.  This screen is to remind you that you are

just evaluating this program and that if you continue to use the program

you must register.  (Registered users will NOT have this screen)  To continue

just press any key.

After pressing any key you will now view the main menu.  Press the

right or left arrow key and watch how the menu points to the following

menu topics:

Fluid Flow Calculations

Hydraulic Radius

Properties

Options

Exit

Stop the pointer at <Fluid Flow Calculations> and then press <enter>.

By the way, any time you want to get to the main menu all you have

to do is press the <esc> key a few times depending on how deep into the

program you have gone.  Another way to choose the topic is to point at

the topic with the mouse and then press the left key of the mouse.  You

could have also pressed <alt> f.

============================================================================

Fluid Flow Cal Version 1.2  Copyright 1992 by Frank DeBlanc   Page 6

============================================================================

I will now explain each menu topic.

=================================

A.  Fluid Flow Calculations Topic

=================================

Point to Fluid Flow Calculations and press <enter>.  You are given

the following subtopics.

Head Loss

Fluid Flow

Pipe Diameter

Two Parallel Pipes

Two Series Pipes

Head Loss-Non-Cir

Fluid Flow-Non-Cir

Diameter-Non-Cir

To point to the desired subtopic press the up arrow or the down

arrow key then press <enter> when you have arrived at the subtopic

of your choice.  (Or point to the subtopic with the mouse and press

the left mouse button).

1.  Subtopic:  Head Loss - head loss is the unknown.  Use only with full-

flowing circular pipes.

Data Needed:  flow rate (cubic ft/sec, cubic ft/min,

gal/sec, gal/min)

pipe diameter (inch)

specific weight (lbf/cubic ft)

absolute viscosity (lbf-sec/sq.ft)

pipe length (feet)

absolute roughness (feet)

After roughness is input the result should appear.  If you

want a printed copy just press the <print screen> key.  Always check

the data that is displayed to be sure that it is the same data you

input and also, if the results seem reasonable.

Note:  <Esc> key will always bring you to the previous screen or

to the main menu.

2.  Subtopic - Fluid Flow - fluid flow rate is unknown.  Use only with

full-flowing circular pipes.

Data Needed:  head loss (feet)

pipe diameter (inches)

specific weight (lbf/cubic foot)

absolute viscosity (lbf-sec/sq.ft)

pipe length (feet)

absolute roughness (feet)

============================================================================

Fluid Flow Cal Version 1.2  Copyright 1992 by Frank DeBlanc   Page 7

============================================================================

3.  Subtopic - Pipe Diameter - pipe diameter is unknown.  Use only with full-

flowing circular pipes.

Data Needed:  flow rate (cubic ft/sec,

cubic ft/min,

gal/sec, gal/min)

head loss (feet)

specific weight (lbf/cubic ft)

absolute viscosity (lbf-sec/sq.ft.)

pipe length (feet)

absolute roughness (feet)

4.  Subtopic - Two parallel pipes.  Use only with two full flowing circular

pipes.

The objective of two parallel pipes is to determine the division

of flow in each pipe given the total flow rate.  It can be seen that the

head loss will be the same in each pipe because the pressure difference

is the same.

Data Needed: diameter of pipe 1  (inch)

diameter of pipe 2  (inch)

pipe length pipe 1  (feet)

pipe length pipe 2  (feet)

flow rate  (cubic feet/min, cubic feet/sec

gal/min, gal/sec)

specific weight  (lbf/cubic ft)

absolute viscosity  (lbf-sec/sq.ft.)

absolute roughness of pipe 1  (feet)

absolute roughness of pipe 2  (feet)

5.  Subtopic - Two series pipes.  Use only with two full-flowing circular

pipes.

The objective of two series pipes is to determine flow rate.

(Note:  If the flow rate is known then the friction loss can be found

easily as the sum of the friction losses in the sections).

Data Needed: diameter of pipe 1  (inch)

diameter of pipe 2  (inch)

pipe length pipe 1  (feet)

pipe length pipe 2  (feet)

specific weight  (lbf/cubic ft)

absolute viscosity  (lbf-sec/sq.ft.)

absolute roughness of pipe 1  (feet)

absolute roughness of pipe 2  (feet)

head loss total  (feet)

============================================================================

Fluid Flow Cal Version 1.2  Copyright 1992 by Frank DeBlanc   Page 8

============================================================================

6.  Subtopic:  Head Loss - head loss is the unknown.  Use for non-

circular conduits. (or partially full circular)

Data Needed:  flow rate (cubic ft/sec, cubic ft/min,

gal/sec, gal/min)

equivalent pipe diameter (inch)

specific weight (lbf/cubic ft)

absolute viscosity (lbf-sec/sq.ft)

area (square feet)

pipe length (feet)

absolute roughness (feet)

7.  Subtopic - Fluid Flow - fluid flow rate is unknown.  Use for non-

circular conduits.  (or partially full circular)

Data Needed:  head loss (feet)

equivalent pipe diameter (inches)

specific weight (lbf/cubic foot)

absolute viscosity (lbf-sec/sq.ft)

pipe length (feet)

absolute roughness (feet)

area (square feet)

8.  Subtopic - Pipe Diameter (EQUIVALENT)

- Equivalent diameter is unknown.  Use for non-

circular conduits. (or partially full circular)

Data Needed:  flow rate (cubic ft/sec,

cubic ft/min,

gal/sec, gal/min)

head loss (feet)

specific weight (lbf/cubic ft)

absolute viscosity (lbf-sec/sq.ft.)

pipe length (feet)

absolute roughness (feet)

area (square feet)

==========================

B.  Hydraulic Radius Topic

==========================

Hydraulic radius topic has the following subtopics:

Partially Full Circle

Partially Full Rectangle

Partially Full Triangle

Partially Full Trapezoid

Full Flowing Trapezoid

Full Flowing Square

Full Flowing Rectangle

Full Flowing Annulus

============================================================================

Fluid Flow Cal Version 1.2  Copyright 1992 by Frank DeBlanc   Page 9

============================================================================

1.  Partially Full Circle  -  radius (inch)

height of fluid (inch)

2.  Partially Full Rectangle  -  height of fluid (inch)

width (inch)

3.  Partially Full Triangle  -  isosceles triangle with the base as the width.

height of fluid (inch)

width (inch)

4.  Partially Full Trapezoid  -  isosceles trapezoid

height of fluid (inch)

top width (inch)

bottom width (inch)

5.  Full Flowing Square  -  height of fluid (inch)

6.  Full Flowing Rectangle  -  height of fluid (inch)

width of fluid (inch)

7.  Full Flowing Annulus  -  inside pipe diameter (inch)

outside pipe diameter (inch)

When solving for hydraulic radius the equivalent diameter is

also calculated.  The value for the equivalent diameter becomes the

default diameter value.

====================

C.  Properties Topic

====================

1.  Water  -  Temperature Range is:  40 to 212, inclusive

Data:  Specific Weight (lbf/cubic ft)

Dynamic (absolute) viscosity (lbf-sec/sq.ft.)

Point to the value you need with the up/down arrow keys or click

with left mouse button.  This will cause the data to become default

values.

2.  Air  -  Temperature Range is:  0 to 250, inclusive

Data:  Specific Weight (lbf/cubic ft)

Dynamic (absolute) viscosity (lbf-sec/sq.ft.)

Point to the value you need with the up/down arrow keys or click

with left mouse button.  This will cause the data to become default

values.

============================================================================

Fluid Flow Cal Version 1.2  Copyright 1992 by Frank DeBlanc   Page 10

============================================================================

==================

D.  Options Topic

==================

Use the up or down arrow keys to point to Background Color or

Foreground Color.  Press <enter> to toggle the different colors.

You could also point with the mouse and press the left mouse button

to toggle values.  Once you leave the options topic the colors will

take effect. <esc> to exit options topic.

---------------------------------------------------------------------------

XI.  Examples

---------------------------------------------------------------------------

====================

A.  Circular Conduit

====================

In the following examples I will assume you are initially pointing

at the topic "Fluid Flow Calculations" of the main menu without

any subtopic showing.

1.  Solve for head loss

Example:   Determine the head loss for the flow of 1,500 gpm of water

at 50 F through 450 feet of cast-iron pipe having an internal

diameter of 10 inches.

Press <right arrow> twice  ---->  Points to Properties Topic

Press <enter>              ---->  Sub-Topic of Menu Shows

Press <enter>              ---->  Shows water data

Press <up arrow> twice     ---->  Points to 50 F data

Press <enter>              ---->  Returns to main menu with 50 F

data as default values.

Press <enter>              ---->  Shows sub-topics

Press <enter>              ---->  Picks Head Loss

Press <down arrow> 3 times ---->  Points of gpm

Press <enter>              ---->  Shows input box for gal/min

1500 <enter>               ---->  input flow rate

10 <enter>                 ---->  input diameter

Press <enter>              ---->  do not input any number.  By

pressing just enter you are

using the default value.

Press <enter>              ---->  same as above

450 <enter>                ---->  input length of pipe

.00085 <enter>             ---->  for cast iron pipe (roughness)

**************************

*  Head Loss =  6.46 ft  *

**************************

============================================================================

Fluid Flow Cal Version 1.2  Copyright 1992 by Frank DeBlanc   Page 11

============================================================================

2.  Solve for fluid flow

Example:  Gasoline (sp gr 0.68) at 60 F flows through a 6 in Schedule

40 welded-steel pipe with a head loss of 10 ft in 5000 ft.

Determine the flow.

<enter>                    ---->  reveal subtopics

<down arrow> once          ---->  point to Fluid Flow

<enter>                    ---->  pick Fluid Flow

10 <enter>                 ---->  head loss is 10 ft

6.065 <enter>              ---->  inside diameter of pipe

42.43 <enter>              ---->  specific weight (.68 x 62.4)

0.00000659 <enter>         ---->  viscosity of gasoline at 60 F

or

6.59d-6 <enter>

5000 <enter>               ---->  length of pipe.

0.00015 <enter>            ---->  roughness of steel

***********************************

* Fluid Flow = 0.384 cubic ft/sec *

***********************************

3.  Solve for diameter

Example:  Water at 60 F is to flow at the rate of 500 cubic feet/sec

through a concrete pipe 5000 ft long with head loss of

no more than 50 feet.  Determine the diameter of the pipe.

<right arrow> twice   ------->  point to properties topic

<enter>               ------->  reveals subtopic

<enter>               ------->  picks water & reveals table

<up arrow> once       ------->  point to properties of water, 60 F

<enter>               ------->  sets data of water as default

<enter>               ------->  reveals subtopics

<down arrow> twice    ------->  points to Pipe Diameter topic

<enter>               ------->  picks Pipe Diameter

<enter>               ------->  pick cfs

500 <enter>           ------->  input flow rate

50 <enter>            ------->  input head loss

<enter>               ------->  input default specific weight

<enter>               ------->  input default absolute viscosity

5000 <enter>          ------->  input length of pipe

.003 <enter>           ------->  input roughness

*************************

* Diameter = 76.33 inch *

*************************

============================================================================

Fluid Flow Cal Version 1.2  Copyright 1992 by Frank DeBlanc   Page 12

============================================================================

========================

B.  Non-Circular Conduit

========================

1.  Solve for head loss

Example:  Air (T = 80 F and p = 14.7 psia) flows at a rate of 4,800 cfm

in a 1x2 ft commercial steel rectangular duct.  What is the

pressure drop per 100 ft of duct?

<right arrow> once     ----->  Hydraulic radius topic

<enter>                ----->  subtopics

<down arrow> 5 times   ----->  Full flowing rectangle

<enter>                ----->  Picks full flowing rectangle

12 <enter>             ----->  1 ft height

24 <enter>             ----->  2 ft width

Eq. diameter = 16 inches

<enter>

<enter>

<down arrow> 5 times   ----->  point to head loss-non cir

<enter>

<down arrow> once      ----->  point to cfm

<enter>

4800 <enter>           ----->  input 4800 cfm

<enter>                ----->  default value   16"

.0735 <enter>          ----->  specific weight

.000000385 <enter>     ----->  absolute viscosity

2 <enter>              ----->  area of duct

100 <enter>            ----->  length of pipe

.00015 <enter>         ----->  steel roughness

**********************

* head loss = 28.748 *

**********************

============================================================================

Fluid Flow Cal Version 1.2  Copyright 1992 by Frank DeBlanc   Page 13

============================================================================

2.  Solve for fluid flow

Example:  Air (T = 60 F and p = 14.7 psia) flows through a 1x2 ft

commercial steel rectangular duct with a head loss of 10 ft

in 300 feet.  Determine the flow.

<right arrow> once     ----->  hydraulic radius topic

<enter>                ----->  reveals subtopics

<down arrow> 5 times   ----->  points to full flowing rectangle

<enter>

12 <enter>             ----->  enter height of duct

24 <enter>             ----->  enter width of duct

equivalent diameter = 16"

<enter>

<right arrow> twice    ----->  points to properties topic

<enter>                ----->  reveals subtopics

<down arrow> once      ----->  point to air

<enter>

<enter>                ----->  pick properties of air at 60 F

<enter>                ----->  reveals subtopics

<down arrow> 6 times   ----->  point to fluid flow-non cir

<enter>

10 <enter>             ----->  enter head loss

<enter>                ----->  16" default

<enter>                ----->  specific weight default

<enter>                ----->  absolute viscosity default

300 <enter>            ----->  pipe length

.00015 <enter>         ----->  roughness of steel

<enter>                ----->  area default

***********************************

* Fluid Flow Rate  =  1496.67 cfm *

***********************************

============================================================================

Fluid Flow Cal Version 1.2  Copyright 1992 by Frank DeBlanc   Page 14

============================================================================

3.  Solve for fluid flow - open channel flow

Example:  Solve for the discharge of water (60 F) that a

10-ft-wide channel can carry if the depth of the

flow is 6 ft and the slope of the channel

is 0.002.  The channel is made of concrete.

slope of channel equals to (head loss) divided by (length).

therefore:  assume  head loss = 0.002 ft

length    = 1 ft

<right arrow> once     ----->  hydraulic radius topic

<enter>                ----->  reveals subtopics

<down arrow> 1 time    ----->  points to partially full rectangle

<enter>

72 <enter>             ----->  enter height of channel

120 <enter>            ----->  enter width of channel

equivalent diameter = 130.909090901

<enter>

<right arrow> twice    ----->  points to properties topic

<enter>                ----->  reveals subtopics

<enter>                ----->  picks water properties

<up arrow> once        ----->  points to water at 60 F

<enter>                ----->  pick properties of water at 60 F

<enter>                ----->  reveals subtopics

<down arrow> 6 times   ----->  point to fluid flow-non cir

<enter>

.002 <enter>           ----->  enter head loss

<enter>                ----->  default for equivalent diameter

<enter>                ----->  specific weight default

<enter>                ----->  absolute viscosity default

1 <enter>              ----->  channel length

.003 <enter>           ----->  roughness of concrete

<enter>                ----->  area default

***********************************

* Fluid Flow Rate  = 585.3711 cfs *

***********************************

============================================================================

Fluid Flow Cal Version 1.2  Copyright 1992 by Frank DeBlanc   Page 15

============================================================================

======================

C.  Two parallel pipes

======================

Example:  With a total flow of 14 cfs, determine the division of

flow and the loss of head for pipe 1 and pipe 2 in

parallel.  Fluid is water at 70 F.

Pipe 1                Pipe 2

D = 18 in           D = 12 in

L = 5000 ft         L = 2000 ft

steel pipe          steel pipe

<enter>                ------>  reveals subtopics

<down arrow>  3 times  ------>  subtopic two parallel pipes

<enter>

18 <enter>             ------>  diameter of pipe one

12 <enter>             ------>  diameter of pipe two

5000 <enter>           ------>  length of pipe one

2000 <enter>           ------>  length of pipe two

<enter>

14 <enter>             ------>  input flow rate

62.3 <enter>           ------>  input specific weight

.0000205 <enter>       ------>  input absolute viscosity

.00015 <enter>         ------>  roughness pipe 1

.00015 <enter>         ------>  roughness pipe 2

***************************************

* pipe 1 flow = 8.9897 cubic feet/sec *

* pipe 2 flow = 5.0103 cubic feet/sec *

* Total       = 14.000 cubic feet/sec *

***************************************

============================================================================

Fluid Flow Cal Version 1.2  Copyright 1992 by Frank DeBlanc   Page 16

============================================================================

====================

D.  Two series pipes

====================

Example:  In the last example the two pipes were in parallel.  Suppose

the same two pipes are now in series.  To get the same head

loss as the last example what must the flow rate be?

<enter>                ------>  reveals subtopics

<down arrow>  4 times  ------>  subtopic two series pipes

<enter>

18 <enter>             ------>  diameter of pipe one

12 <enter>             ------>  diameter of pipe two

5000 <enter>           ------>  length of pipe one

2000 <enter>           ------>  length of pipe two

62.3 <enter>           ------>  input specific weight

.0000205 <enter>       ------>  input absolute viscosity

.00015 <enter>         ------>  roughness pipe 1

.00015 <enter>         ------>  roughness pipe 2

18.5661643946 <enter>  ------>  enter head loss in ft

*************************************

* Flow rate = 4.3062 cubic feet/sec *

*************************************